## AF - QC 05 - Section Details
|  | Quality Control Report 05: |  |  |  |  | Report Generated From BUILDER SMS on:
|  | SECTION DETAILS |  |  |  |  | 2022-05-24 10:58
Kirtland AFB
Complex Name | Building Number | Building Name | Year Built | Building Area | UoM | Floors | System | Component | Material/Equipment Category | Component Subtype | Section Name | Section Quantity | Section UoM | Section Install Date | Install Date Source | Design Life (DL) | Section Age | Section RDL | RSL (Years) | Painted? | Paint Year | Section CI | Paint CI | Inventory Section Comments | ID Number | Equipment Type | Equipment Make | Model | Serial Number | Capacity | Manufacturer | Date Manufactured | Date Installed | Control Type Make | Warranty Date | Warranty Company | Location | Comment | Warranty Date 2 | Warranty Company 2 | Number of Detail Images
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2010 EXTERIOR WALLS | B201001 EXTERIOR CLOSURE | Concrete Block | EXT WALL CON BLK 1 | 339 | SF | 1974 | Input | 75 | 48 | 27 | 27.1725 | TRUE | 2014 | 75.6352
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2010 EXTERIOR WALLS | B201001 EXTERIOR CLOSURE | Metal Panel | EXT WALL MET PAN 1 | 3285 | SF | 1974 | Input | 30 | 48 | -18 | 5.4309 | FALSE |  | 58.9245
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2030 EXTERIOR DOORS | B203001 SOLID DOORS | Steel | EXT DR STL 1 | 2 | EA | 2014 | Estimated | 20 | 8 | 12 | 4.383 | FALSE |  | 59.4769
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2030 EXTERIOR DOORS | B203004 OVERHEAD AND ROLL-UP DOORS | Steel Rolling, Manual, 12'x12' | EXT OVRHD MAN DR 1 | 1 | EA | 2014 | Estimated | 20 | 8 | 12 | 4.383 | FALSE |  | 59.4769 |  |  | MHMV019879 |  |  | NA | NA | 12 FT X 12 FT | NA | [5 empty] | EXTERIOR |  |  |  | 3
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | B30 ROOFING | B3010 ROOF COVERINGS | B301001 STEEP SLOPE ROOF SYSTEMS | Formed Metal | ROOF STEEP MET 1 | 1368 | SF | 1974 | Input | 30 | 48 | -18 | 8.5265 | FALSE |  | 69.6689
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | C30 INTERIOR FINISHES | C3020 FLOOR FINISHES | C302001 TILE FLOOR FINISHES | General | INT FLR ASBSTS TILE 1 | 45 | SF | 1974 | Input | 75 | 48 | 27 | 0 | FALSE |  | 10
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | C30 INTERIOR FINISHES | C3020 FLOOR FINISHES | C302009 FLOOR TOPPINGS AND TRAFFIC MEMBRANES | Paint | INT FLR PNT 1 | 1260 | SF | 2014 | Estimated | 20 | 8 | 12 | 4.383 | FALSE |  | 59.4769
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | C30 INTERIOR FINISHES | C3030 CEILING FINISHES | C303090 OTHER CEILING & CEILING FINISHES | Exposed Concrete Finish | INT CEIL CON 1 | 45 | SF | 1974 | Input | 125 | 48 | 77 | 47.8904 | FALSE |  | 77.0844
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | C30 INTERIOR FINISHES | C3030 CEILING FINISHES | C303090 OTHER CEILING & CEILING FINISHES | Plastic Covered Insulated Batts | INT CEIL PLSTC 1 | 4653 | SF | 2014 | Estimated | 20 | 8 | 12 | 4.383 | FALSE |  | 59.4769 |  | [Jeffrey Scott on 7/27/2018 12:52:39 PM] THIS VALUE REPRESENTS THE COVER FOR THE CEILING AND THE WALLS. THE INSULATED BATTS COVER BOTH
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | D20 PLUMBING | D2090 OTHER PLUMBING SYSTEMS | D209005 COMPRESSED AIR SYSTEM (NON-BREATHING) | General | MECH PLMB COMP AIR 1 | 1 | EA | 2004 | Input | 25 | 18 | 7 | 9.2401 | FALSE |  | 76.7433 |  | [Matthew Vella on 6/27/2018 9:31:27 AM] THIS UNIT IS AN AIR COMPRESSOR. | MHMV039724 |  |  | VRV7F-8 | DM020494 | 7.5 HP 80 GAL EST TANK | CHAMPION PNEUMATIC | [5 empty] | SOUTH EXTERIOR MECH ROOM |  |  |  | 3
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 100 amp, NQOD | EXT PNLBRD MAIN 1 | 1 | EA | 1985 | Input | 40 | 37 | 3 | 0.10863 | FALSE |  | 40.2621 |  |  | MHMV019897 |  |  | NA | AG 337217 | 100 A | SQUARE D |  | 1985 |  |  |  | SOUTH EXTERIOR |  |  |  | 2
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 200 Amp | EXT PNLBRD SFTY SWTCH 1 | 1 | EA | 1985 | Input | 40 | 37 | 3 | 8.5426 | FALSE |  | 61.7046 |  | [Adam Nodel on 7/13/2018 7:29:50 AM] NO DATA PLATE WAS AVAILABLE FOR THIS SWITCH BECAUSE THE ENCLOSURE HAS BEEN PAINTED. THE RATING GIVEN IS ESTIMATED. | MHMV019896 |  |  | NA | NA | 200 A EST | NA |  | 1985 |  |  |  | SOUTH EXTERIOR |  |  |  | 2
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | EXT PNLBRD SFTY SWTCH 2 | 1 | EA | 1985 | Input | 40 | 37 | 3 | 12.6701 | FALSE |  | 71.9842 |  |  | MHMV019899 |  |  | D 321 N | NA | 30 A | SQUARE D |  | 1985 |  |  |  | SOUTH EXTERIOR MECH ROOM |  |  |  | 2
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502001 BRANCH WIRING | General | INT ELEC BRANCH WRNG 1 | 1408 | SF | 1974 | Input | 60 | 48 | 12 | 20.9572 | FALSE |  | 74.7049
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Interior Lighting, Fluorescent | INT LTNG FLUOR 1 | 4 | EA | 2005 | Input | 20 | 17 | 3 | 6.6112 | FALSE |  | 73.7315
TO BE DEMOED | 00378 | HAZARD STOR, BSE | 1974 | 1408 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Explosion Proof Lighting | INT LTNG INCAN 1 | 1 | EA | 1985 | Input | 20 | 37 | -17 | 0 | FALSE |  | 30
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2010 EXTERIOR WALLS | B201001 EXTERIOR CLOSURE | Wall Louver | EXT WALL LOUV 1 | 32 | SF | 1954 | Input | 30 | 68 | -38 | 0 | TRUE | 1980 | 32.7613
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2010 EXTERIOR WALLS | B201001 EXTERIOR CLOSURE | Metal Panel | EXT WALL MET 1 | 4620 | SF | 1954 | Input | 30 | 68 | -38 | 0 | FALSE |  | 30
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2020 EXTERIOR WINDOWS | B202001 WINDOWS | Steel Windows | EXT WIN STL 1 | 24 | EA | 1954 | Input | 50 | 68 | -18 | 0 | TRUE | 1954 | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2030 EXTERIOR DOORS | B203001 SOLID DOORS | Wood | EXT DR WD 1 | 1 | EA | 1954 | Input | 20 | 68 | -48 | 0 | TRUE | 1954 | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2030 EXTERIOR DOORS | B203004 OVERHEAD AND ROLL-UP DOORS | Steel Rolling, Manual, 20'x12' | EXT OVRHD MAN 1 | 6 | EA | 1954 | Input | 20 | 68 | -48 | 0 | TRUE | 1980 | 30
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2030 EXTERIOR DOORS | B203004 OVERHEAD AND ROLL-UP DOORS | Steel Rolling, Manual, 20'x12' | EXT OVRHD MAN 2 | 4 | EA | 1954 | Input | 20 | 68 | -48 | 0 | TRUE | 1980 | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | B30 ROOFING | B3010 ROOF COVERINGS | B301001 STEEP SLOPE ROOF SYSTEMS | Formed Metal - Metal Standing Seam | ROOF STEEP MET 1 | 11523 | SF | 2008 | Input | 40 | 14 | 26 | 21.3566 | TRUE | 2008 | 87.5217 |  |  | NA | METAL |  | NA | NA | 11523 SF | CREGO METAL SYSTEMS |  | 2008 |  | 2008-11-25 | CREGO METAL SYSTEMS 10 YR | ROOF |  | 2008-11-25 | VIKING ROOFING 1 YR
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | B30 ROOFING | B3010 ROOF COVERINGS | B301005 GUTTERS & DOWNSPOUTS | Downspouts | ROOF GD DWNSPT 1 | 38 | LF | 1980 | Input | 20 | 42 | -22 | 0 | FALSE |  | 34.6399
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | B30 ROOFING | B3010 ROOF COVERINGS | B301005 GUTTERS & DOWNSPOUTS | Gutters | ROOF GD GTTR 1 | 99 | LF | 1980 | Input | 20 | 42 | -22 | 0 | FALSE |  | 24.8405
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | C10 INTERIOR CONSTRUCTION | C1010 PARTITIONS | C101001 FIXED PARTITIONS | General | INT PART CON BLK 1 | 1200 | SF | 1954 | Input | 50 | 68 | -18 | 0 | TRUE | 1980 | 39.5978
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | C10 INTERIOR CONSTRUCTION | C1010 PARTITIONS | C101001 FIXED PARTITIONS | Wall - Drywall w/Stud Framing | INT PART DRYWL 1 | 3627 | SF | 1954 | Input | 50 | 68 | -18 | 0 | TRUE | 1980 | 30
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | C10 INTERIOR CONSTRUCTION | C1020 INTERIOR DOORS | C102001 STANDARD INTERIOR DOORS | General | INT DR MET 1 | 1 | EA | 1954 | Input | 40 | 68 | -28 | 0 | TRUE | 1980 | 30
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | C10 INTERIOR CONSTRUCTION | C1020 INTERIOR DOORS | C102001 STANDARD INTERIOR DOORS | Wood Door/Wood Frame | INT DR WD WD 1 | 22 | EA | 1954 | Input | 40 | 68 | -28 | 0 | TRUE | 1980 | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | C10 INTERIOR CONSTRUCTION | C1030 SPECIALTIES | C103001 COMPARTMENTS, CUBICLES & TOILET PARTITIONS | Toilet Partitions | INT PART TOILET 1 | 2 | EA | 1954 | Input | 20 | 68 | -48 | 0 | TRUE | 1954 | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | C30 INTERIOR FINISHES | C3020 FLOOR FINISHES | C302001 TILE FLOOR FINISHES | Ceramic Tile | INT FLR TILE 1 | 259 | SF | 1954 | Input | 75 | 68 | 7 | 0 | FALSE |  | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | C30 INTERIOR FINISHES | C3020 FLOOR FINISHES | C302005 CARPETING | Carpet Tile | INT FLR CRPT 1 | 2214 | SF | 1954 | Input | 10 | 68 | -58 | 0 | FALSE |  | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | C30 INTERIOR FINISHES | C3020 FLOOR FINISHES | C302009 FLOOR TOPPINGS AND TRAFFIC MEMBRANES | Paint | INT FLR PAINT 1 | 7319 | SF | 1954 | Input | 20 | 68 | -48 | 0 | TRUE | 1980 | 24.4584
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | C30 INTERIOR FINISHES | C3030 CEILING FINISHES | C303002 GYPSUM WALLBOARD CEILING FINISHES | General | INT CEIL GYPS 1 | 9792 | SF | 1954 | Input | 125 | 68 | 57 | 47.696 | FALSE |  | 77.2079
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D20 PLUMBING | D2010 PLUMBING FIXTURES | D201001 WATERCLOSETS | General | INT FIXTR WTRCLST 1 | 3 | EA | 1990 | Input | 25 | 32 | -7 | 0 | FALSE |  | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D20 PLUMBING | D2010 PLUMBING FIXTURES | D201002 URINALS | General | INT FIXTR URNL 1 | 2 | EA | 1990 | Input | 25 | 32 | -7 | 0 | FALSE |  | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D20 PLUMBING | D2010 PLUMBING FIXTURES | D201003 LAVATORIES | General | INT FIXTR LAV 1 | 3 | EA | 1990 | Input | 25 | 32 | -7 | 0 | FALSE |  | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D20 PLUMBING | D2010 PLUMBING FIXTURES | D201005 SHOWERS/TUBS | Bathtub | INT FIXTR SHWR 1 | 1 | EA | 1990 | Input | 25 | 32 | -7 | 0 | FALSE |  | 10
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D20 PLUMBING | D2020 DOMESTIC WATER DISTRIBUTION | D202003 DOMESTIC WATER EQUIPMENT | Water Heaters, Residential, Gas | FLR1 WTR HTR RES GAS 1 | 1 | EA | 1990 | Input | 25 | 32 | -7 | 0 | FALSE |  | 10 |  |  | MHMV009708 |  |  | CV 40 NRT8 DH | A8097085 | 40 GAL | STATE SELECT |  | 1990 |  |  |  | WEST INTERIOR |  |  |  | 3
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D20 PLUMBING | D2090 OTHER PLUMBING SYSTEMS | D209005 COMPRESSED AIR SYSTEM (NON-BREATHING) | General | MECH PLMB COMP AIR 1 | 1 | EA | 1990 | Estimated | 25 | 32 | -7 | 0 | FALSE |  | 10 |  |  | MHMV009709 |  |  | NA | NA | 100 GAL EST | SAYLOR-BEALL |  | 1990 |  |  |  | WEST EXTERIOR |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D30 HVAC | D3010 ENERGY SUPPLY | D301002 GAS SUPPLY SYSTEM | Gas Meter | EXT GAS SUP MTR 1 | 1 | EA | 1990 | Input | 50 | 32 | 18 | 0 | FALSE |  | 10 |  |  | MHMV009710 |  |  | AC-250 | 04E410310 | 250 CFH | AMERICAN METER CO. |  | 1990 |  |  |  | SW EXTERIOR |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D30 HVAC | D3020 HEAT GENERATING SYSTEMS | D302001 BOILERS | Gas, Hot Water - 400-500 MBH | MECH BLR GAS HT WTR 1 | 1 | EA | 1990 | Input | 30 | 32 | -2 | 0 | FALSE |  | 10 |  | [Matthew Vella on 3/7/2017 10:49:15 AM] THE DATA PLATE WAS INACCESSIBLE. | MHMV009673 |  |  | NA | NA | 450 MBH EST | NA |  | 1990 |  |  |  | MECH RM | [Matthew Vella on 3/7/2017 8:35:21 AM] THIS UNIT WAS INACCESSIBLE. |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D30 HVAC | D3020 HEAT GENERATING SYSTEMS | D302004 AUXILIARY EQUIPMENT | Expansion Tank - 15 gal | MECH AUX EXP TNK 1 | 1 | EA | 1990 | Input | 30 | 32 | -2 | 0 | FALSE |  | 10 |  | [Matthew Vella on 4/5/2017 8:30:23 AM] THIS UNIT WAS INACCESSIBLE. | NA |  |  | NA | NA | 15 GAL EST | NA |  | 1990 |  |  |  | MECH RM | [Matthew Vella on 3/7/2017 8:35:21 AM] THIS UNIT WAS INACCESSIBLE. |  |  | 1
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D30 HVAC | D3040 DISTRIBUTION SYSTEMS | D304003 HOT WATER DISTRIBUTION SYSTEMS | Circulating Pump, End Suction - 2-1/2" size, 3 HP, to 150 GPM | MECH HOT WTR CIRC PUMP 1 | 1 | EA | 2008 | Input | 20 | 14 | 6 | 0 | FALSE |  | 10 |  |  | MHMV009711 |  |  | NA | 172718 | 3/4 HP, 2 X 5 - 1/4 | BELL & GOSSETT |  | 2008 |  |  |  | MECH RM |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D30 HVAC | D3040 DISTRIBUTION SYSTEMS | D304007 EXHAUST SYSTEMS | Fan System, Wall Exhaust - Wall Exhaust, 26,250 CFM | INT DISTR WALL EXH 1 | 2 | EA | 1990 | Estimated | 10 | 32 | -22 | 0 | FALSE |  | 10 |  | [Matthew Vella on 3/7/2017 8:35:21 AM] THESE UNITS WERE OUT OF REACH. | NA |  |  | NA | NA | 25,000 CFM EST | NA |  | 1990 |  |  |  | SOUTH INTERIOR | [Matthew Vella on 3/7/2017 8:35:21 AM] THESE UNITS WERE OUT OF REACH. |  |  | 1
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D30 HVAC | D3040 DISTRIBUTION SYSTEMS | D304007 EXHAUST SYSTEMS | Fan System, Wall Exhaust - Wall Exhaust, 6175 CFM | INT DISTR WALL EXH 2 | 1 | EA | 1990 | Estimated | 10 | 32 | -22 | 0 | FALSE |  | 10 |  | [Matthew Vella on 3/7/2017 8:35:21 AM] THIS UNIT WAS OUT OF REACH. | NA |  |  | NA | NA | 6175 CFM EST | NA |  | 1990 |  |  |  | NORTH INTERIOR | [Matthew Vella on 3/7/2017 8:35:21 AM] THIS UNIT WAS OUT OF REACH. |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305004 FIN TUBE RADIATION | Baseboard Heating - 8' long | FLR1 FTR BSBRD 1 | 10 | EA | 1954 | Estimated | 30 | 68 | -38 | 0 | FALSE |  | 10 |  | [Matthew Vella on 3/7/2017 8:39:34 AM] NO FURTHER INFORMATION IS AVAILABLE ON THESE UNITS. | NA |  |  | NA | NA | 8' | NA |  | 1954 |  |  |  | INTERIOR | [Matthew Vella on 3/7/2017 8:39:34 AM] NO FURTHER INFORMATION IS AVAILABLE ON THESE UNITS. |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305006 PACKAGE UNITS | Evaporative Cooler - 2740 CFM | EXT PACK EVAP 1 | 2 | EA | 1990 | Estimated | 20 | 32 | -12 | 0 | FALSE |  | 10 |  | [Matthew Vella on 3/7/2017 10:55:37 AM] THIS UNIT WAS OUT OF REACH. ITS SIZE IS ESTIMATED. | NA |  |  | NA | NA | 2740 CFM EST | NA |  | 1990 |  |  |  | SOUTH EXTERIOR | [Matthew Vella on 3/7/2017 10:55:37 AM] THIS UNIT WAS OUT OF REACH. ITS SIZE IS ESTIMATED. |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305006 PACKAGE UNITS | Evaporative Cooler - 4215 CFM | EXT PACK EVAP 2 | 3 | EA | 1990 | Estimated | 20 | 32 | -12 | 0 | FALSE |  | 10 |  | [Matthew Vella on 3/7/2017 10:55:37 AM] THIS UNIT WAS OUT OF REACH. ITS SIZE IS ESTIMATED. | NA |  |  | NA | NA | 4215 CFM EST | NA |  | 1990 |  |  |  | WEST EXTERIOR | [Matthew Vella on 3/7/2017 10:55:37 AM] THIS UNIT WAS OUT OF REACH. ITS SIZE IS ESTIMATED. |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D40 FIRE PROTECTION | D4010 FIRE ALARM AND DETECTION SYSTEMS | D401002 FIRE ALARM DEVICES | Manual pull station | FLR1 FIRE PULL 1 | 3 | EA | 2000 | Estimated | 20 | 22 | -2 | 5.3053 | FALSE |  | 68.3062
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D40 FIRE PROTECTION | D4010 FIRE ALARM AND DETECTION SYSTEMS | D401002 FIRE ALARM DEVICES | Strobe | FLR1 FIRE STBE 1 | 3 | EA | 2000 | Estimated | 20 | 22 | -2 | 5.3053 | FALSE |  | 68.3062
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | EXT PNLBRD SFTY SWTCH 1 | 4 | EA | 2008 | Estimated | 40 | 14 | 26 | 15.8206 | FALSE |  | 76.4289 |  |  | MHMV017165 |  |  | NA | NA | 30A | FEDERAL NOARK |  | 2008 |  |  |  | EXTERIOR EAST |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | EXT PNLBRD SFTY SWTCH 1 | 4 | EA | 2008 | Estimated | 40 | 14 | 26 | 15.8206 | FALSE |  | 76.4289 |  |  | MHMV017164 |  |  | NA | NA | 30A | FEDERAL NOARK |  | 2008 |  |  |  | EXTERIOR EAST |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | EXT PNLBRD SFTY SWTCH 1 | 4 | EA | 2008 | Estimated | 40 | 14 | 26 | 15.8206 | FALSE |  | 76.4289 |  |  | MHMV017160 |  |  | NA | NA | 30A | SQUARE D |  | 2008 |  |  |  | EXTERIOR WEST |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | EXT PNLBRD SFTY SWTCH 1 | 4 | EA | 2008 | Estimated | 40 | 14 | 26 | 15.8206 | FALSE |  | 76.4289 |  |  | MHMV017161 |  |  | NA | NA | 30A | SQUARE D |  | 2008 |  |  |  | EXTERIOR WEST |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 400 Amp | EXT PNLBRD SFTY SWTCH 2 | 2 | EA | 1990 | Input | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017159 |  |  | NA | NA | 400A | FEDERAL ELECTRC |  | 1990 |  |  |  | EXTERIOR WEST |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 400 Amp | EXT PNLBRD SFTY SWTCH 2 | 2 | EA | 1990 | Input | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017162 |  |  | NA | NA | 400A | FEDERAL ELECTRC |  | 1990 |  |  |  | EXTERIOR WEST |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 1 | 5 | EA | 1990 | Input | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017143 |  |  | NA | NA | 225A | SQUARE D |  | 1990 |  |  |  | BAY |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 1 | 5 | EA | 1990 | Input | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017157 |  |  | NA | NA | 225A | GENERAL ELECTRIC |  | 1990 |  |  |  | BAY |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 1 | 5 | EA | 1990 | Input | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017144 |  |  | NA | NA | 225A | SQUARE D |  | 1990 |  |  |  | BAY |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 1 | 5 | EA | 1990 | Input | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017139 |  |  | NA | NA | 225A | SIEMENS |  | 1990 |  |  |  | BAY |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 1 | 5 | EA | 1990 | Input | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017152 |  |  | NA | NA | 225A | SQUARE D |  | 1990 |  |  |  | BAY |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/240 V, 100 amp, NQOD | FLR1 PNLBRD MAIN 2 | 1 | EA | 1995 | Estimated | 40 | 27 | 13 | 7.2367 | FALSE |  | 57.9337 |  |  | MHMV017153 |  |  | NA | NA | 100A | SQUARE D |  | 1995 | NA |  |  | INTERIOR RM 10 |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 3 | 1 | EA | 1995 | Input | 40 | 27 | 13 | 11.3641 | FALSE |  | 68.3419 |  |  | MHMV017146 |  |  | NA | NA | 225A | NA |  | 1995 |  |  |  | INTERIOR RM 7 |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 200 Amp | FLR1 PNLBRD SFTY SWTCH 1 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017148 |  |  | NA | NA | 200A | ITE |  | 1990 |  |  |  | INTERIOR RM 10 |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 200 Amp | FLR1 PNLBRD SFTY SWTCH 1 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017151 |  |  | NA | NA | 200A | SQUARE D |  | 1990 |  |  |  | INTERIOR RM |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 200 Amp | FLR1 PNLBRD SFTY SWTCH 1 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017149 |  |  | NA | NA | 200A | SQUARE D |  | 1990 |  |  |  | INTERIOR RM |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 200 Amp | FLR1 PNLBRD SFTY SWTCH 1 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017150 |  |  | NA | NA | 200A | SQUARE D |  | 1990 |  |  |  | INTERIOR RM 7 |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 200 Amp | FLR1 PNLBRD SFTY SWTCH 1 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017142 |  |  | NA | NA | 200A | ITE |  | 1990 |  |  |  | BAY |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 200 Amp | FLR1 PNLBRD SFTY SWTCH 1 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017147 |  |  | NA | NA | 200A | SQUARE D |  | 1990 |  |  |  | INTERIOR RM 10 |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | FLR1 PNLBRD SFTY SWTCH 2 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017141 |  |  | NA | NA | 60A | SQUARE D |  | 1990 |  |  |  | INTERIOR NE CONER |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | FLR1 PNLBRD SFTY SWTCH 2 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017154 |  |  | NA | NA | 60A | ITE |  | 1990 |  |  |  | BAY |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | FLR1 PNLBRD SFTY SWTCH 2 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017156 |  |  | NA | NA | 30A | ITE |  | 1990 |  |  |  | BAY |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | FLR1 PNLBRD SFTY SWTCH 2 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017155 |  |  | NA | NA | 60A | WESTINGHOUSE |  | 1990 |  |  |  | BAY |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | FLR1 PNLBRD SFTY SWTCH 2 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017145 |  |  | NA | NA | 30A | ITE |  | 1990 |  |  |  | INTERIOR WEST |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | FLR1 PNLBRD SFTY SWTCH 2 | 6 | EA | 1990 | Estimated | 40 | 32 | 8 | 3.1286 | FALSE |  | 47.6761 |  |  | MHMV017140 |  |  | NA | NA | 60A | ITE |  | 1990 |  |  |  | INTERIOR NE CONER |  |  |  | 2
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502001 BRANCH WIRING | General | FLR1 ELEC BRANCH WRNG 1 | 11177 | SF | 1990 | Estimated | 60 | 32 | 28 | 26.3251 | FALSE |  | 81.8457
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Exterior Lighting - Metal halide, wall pack, 175 W | EXT LTNG MET HLDE 1 | 12 | EA | 2000 | Estimated | 25 | 22 | 3 | 7.9341 | FALSE |  | 72.6018
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Exit Lighting | FLR1 LTNG EX 1 | 2 | EA | 2000 | Estimated | 25 | 22 | 3 | 7.9341 | FALSE |  | 72.6018
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Interior Lighting, Fluorescent | FLR1 LTNG FLUOR 1 | 120 | EA | 2000 | Estimated | 20 | 22 | -2 | 5.3053 | FALSE |  | 68.3062
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Interior Lighting, Incandescent | FLR1 LTNG INCAN 1 | 4 | EA | 1990 | Estimated | 20 | 32 | -12 | 5.3053 | FALSE |  | 69.2428
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5090 OTHER ELECTRICAL SERVICES | D509002 EMERGENCY LIGHTING & POWER | Emergency Lighting | FLR1 EMERG LTNG 1 | 3 | EA | 2000 | Estimated | 20 | 22 | -2 | 5.2943 | FALSE |  | 68.2522
TO BE DEMOED | 00734 | ELCT RSCH TST | 1954 | 11177 | SF | 1 | D50 ELECTRICAL | D5090 OTHER ELECTRICAL SERVICES | D509004 LIGHTNING PROTECTION | General | ROOF ELEC LTNG PROT 1 | 12 | EA | 1990 | Input | 50 | 32 | 18 | 16.6193 | FALSE |  | 72.9087
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | A10 FOUNDATIONS | A1030 SLAB ON GRADE | A103001 STANDARD SLAB ON GRADE | General | SYS SOG STD 1 | 10350 | SF | 1965 | Input | 100 | 57 | 43 | 65.3955 | FALSE |  | 94.6565
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | A20 BASEMENT CONSTRUCTION | A2020 BASEMENT WALLS | A202001 BASEMENT WALL CONSTRUCTION | CIP Concrete | BASE WALL CON 1 | 66 | LF | 1965 | Input | 100 | 57 | 43 | 51.5283 | FALSE |  | 87.3651
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B20 EXTERIOR ENCLOSURE | B2010 EXTERIOR WALLS | B201001 EXTERIOR CLOSURE | E.I.F.S. | EXT WALL EIFS 1 | 11000 | SF | 1995 | Input | 50 | 27 | 23 | 19.6692 | FALSE |  | 78.2401
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B20 EXTERIOR ENCLOSURE | B2010 EXTERIOR WALLS | B201006 BALCONY WALLS & HANDRAILS | Ladder | EXT BALC LDR 1 | 8 | LF | 2005 | Input | 15 | 17 | -2 | 8.918 | FALSE |  | 92.798 | [5 empty] | MHMV040344 |  |  |  |  | 2005 |  |  |  | 2ND FLR BREEZE WAY
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B20 EXTERIOR ENCLOSURE | B2010 EXTERIOR WALLS | B201006 BALCONY WALLS & HANDRAILS | General | EXT WALL BALC 1 | 131 | LF | 1995 | Input | 15 | 27 | -12 | 5.1667 | TRUE | 2011 | 74.865 | 98.2294
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B20 EXTERIOR ENCLOSURE | B2010 EXTERIOR WALLS | B201007 EXTERIOR SOFFITS | General | EXT WALL SOFF 1 | 3488 | SF | 1995 | Input | 20 | 27 | -7 | 7.2385 | TRUE | 2015 | 76.1109
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B20 EXTERIOR ENCLOSURE | B2020 EXTERIOR WINDOWS | B202001 WINDOWS | Aluminum Windows | EXT WND ALUM 1 | 40 | EA | 1995 | Input | 35 | 27 | 8 | 6.2478 | FALSE |  | 57.9562
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B20 EXTERIOR ENCLOSURE | B2030 EXTERIOR DOORS | B203001 SOLID DOORS | Steel | EXT DR STL 1 | 47 | EA | 2005 | Input | 20 | 17 | 3 | 0.9578 | TRUE | 2005 | 44.6986
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B30 ROOFING | B3010 ROOF COVERINGS | B301002 LOW SLOPE ROOF SYSTEMS | Built-Up | ROOF LOW BLT UP 1 | 10350 | SF | 2005 | Input | 20 | 17 | 3 | 7.2385 | FALSE |  | 75.8482
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B30 ROOFING | B3010 ROOF COVERINGS | B301005 GUTTERS & DOWNSPOUTS | Downspouts | ROOF GD DWNSPTS 1 | 150 | LF | 2005 | Input | 20 | 17 | 3 | 5.1748 | FALSE |  | 66.0988
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B30 ROOFING | B3010 ROOF COVERINGS | B301005 GUTTERS & DOWNSPOUTS | Gutters | ROOF GD GTTRS 1 | 550 | LF | 2005 | Input | 20 | 17 | 3 | 3.1208 | FALSE |  | 55.6963
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | B30 ROOFING | B3010 ROOF COVERINGS | B301006 ROOF OPENINGS AND SUPPORTS | Hatches | ROOF OPEN HATCH 1 | 1 | EA | 2005 | Input | 75 | 17 | 58 | 30.0281 | FALSE |  | 78.4801
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C10 INTERIOR CONSTRUCTION | C1010 PARTITIONS | C101001 FIXED PARTITIONS | Wall - Concrete Block | INT PART CON BLK 1 | 1784 | SF | 1965 | Input | 75 | 57 | 18 | 38.3841 | FALSE |  | 87.2065
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C10 INTERIOR CONSTRUCTION | C1010 PARTITIONS | C101001 FIXED PARTITIONS | Wall - Drywall w/Stud Framing | INT PART DRYWLL 1 | 25280 | SF | 1965 | Input | 50 | 57 | -7 | 19.6692 | FALSE |  | 78.4665
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C10 INTERIOR CONSTRUCTION | C1020 INTERIOR DOORS | C102001 STANDARD INTERIOR DOORS | Wood Door/Metal Frame | INT DR WD MET 1 | 80 | EA | 2005 | Input | 40 | 17 | 23 | 15.5257 | TRUE | 2013 | 77.6491
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C10 INTERIOR CONSTRUCTION | C1020 INTERIOR DOORS | C102004 SLIDING & FOLDING DOORS | General | INT DR 1 | 80 | EA | 2003 | Input | 30 | 19 | 11 | 11.3821 | FALSE |  | 77.1272 |  | [Gerardo Bolivar on 5/5/2021 9:31:02 AM] THESE ARE SLIDING CLOSET DOORS. 2 DOORS PER SET.
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3010 WALL FINISHES | C301003 GYPSUM WALLBOARD FINISHES | General | INT WALL GYPS 1 | 25280 | SF | 2005 | Input | 125 | 17 | 108 | 50.7459 | TRUE | 2021 | 79.1487
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3010 WALL FINISHES | C301004 TILE & TERRAZZO WALL FINISHES | Tile | INT WALL TILE 1 | 1680 | SF | 2005 | Input | 75 | 17 | 58 | 38.3841 | FALSE |  | 86.8274
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3010 WALL FINISHES | C301005 WALL COVERINGS | Wallpaper | INT WALL WLPAPER 1 | 1280 | SF | 2005 | Input | 15 | 17 | -2 | 6.8379 | FALSE |  | 83.9896
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3020 FLOOR FINISHES | C302001 TILE FLOOR FINISHES | Ceramic Tile | INT FLR TILE 1 | 800 | SF | 1995 | Input | 75 | 27 | 48 | 22.2891 | FALSE |  | 69.4983
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3020 FLOOR FINISHES | C302004 RESILIENT FLOOR FINISHES | Resilient Tile | INT FLR VIN 1 | 840 | SF | 1995 | Input | 50 | 27 | 23 | 19.6692 | FALSE |  | 78.2401
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3020 FLOOR FINISHES | C302005 CARPETING | Carpet Tile | INT FLR CRPT 1 | 10982 | SF | 1995 | Input | 10 | 27 | -17 | 0 | FALSE |  | 39.5458
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3020 FLOOR FINISHES | C302010 HARDENERS AND SEALERS | Concrete Topping | INT FLR CON SEAL 1 | 764 | SF | 1965 | Input | 40 | 57 | -17 | 25.529 | FALSE |  | 94.2841
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3030 CEILING FINISHES | C303002 GYPSUM WALLBOARD CEILING FINISHES | General | INT CEIL GYPS 1 | 2240 | SF | 1995 | Input | 125 | 27 | 98 | 50.7459 | FALSE |  | 79.0767
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3030 CEILING FINISHES | C303005 SUSPENSION SYSTEMS | General | INT CEIL SUSP 1 | 10880 | SF | 1995 | Input | 20 | 27 | -7 | 5.1748 | FALSE |  | 66.332
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | C30 INTERIOR FINISHES | C3030 CEILING FINISHES | C303090 OTHER CEILING & CEILING FINISHES | Exposed Concrete Finish | INT CEIL CON 1 | 764 | SF | 1965 | Input | 125 | 57 | 68 | 82.0065 | FALSE |  | 94.706
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D20 PLUMBING | D2010 PLUMBING FIXTURES | D201001 WATERCLOSETS | General | INT FIXTR WTRCLST 1 | 40 | EA | 1987 | Input | 25 | 35 | -10 | 1.4704 | FALSE |  | 45.8473
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D20 PLUMBING | D2010 PLUMBING FIXTURES | D201003 LAVATORIES | General | INT FIXTR LAV 1 | 40 | EA | 1987 | Input | 25 | 35 | -10 | 1.4704 | FALSE |  | 45.8473
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D20 PLUMBING | D2010 PLUMBING FIXTURES | D201004 SINKS | Kitchen Sink | INT SNK KITCH 1 | 20 | EA | 1987 | Input | 35 | 35 | 0 | 2.4736 | FALSE |  | 47.0058
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D20 PLUMBING | D2010 PLUMBING FIXTURES | D201004 SINKS | Service Sink | INT SNK SERV 1 | 1 | EA | 1965 | Input | 25 | 57 | -32 | 1.4704 | FALSE |  | 45.8801
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D20 PLUMBING | D2010 PLUMBING FIXTURES | D201005 SHOWERS/TUBS | General | INT FIXTR SHWR 1 | 40 | EA | 1987 | Input | 25 | 35 | -10 | 1.4704 | FALSE |  | 45.8473
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D20 PLUMBING | D2020 DOMESTIC WATER DISTRIBUTION | D202002 VALVES & HYDRANTS | Backflow Preventer - 1" pipe | MECH VLV BKFLO PREV 1 | 1 | EA | 2006 | Input | 25 | 16 | 9 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2017 9:43:00 AM] A BAR CODE WOULD NOT RELIABLY AFFIX TO THIS BACK FLOW PREVENTER. IT WAS SUBSEQUENTLY PLACED ON ITS ADJACENT MOUNTING BRACKET. | MHMV033954 |  |  | 975XL | W024077 | 0.75 IN | WILKINS-ZURN |  | 2006 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 9:43:00 AM] A BAR CODE WOULD NOT RELIABLY AFFIX TO THIS BACK FLOW PREVENTER. IT WAS SUBSEQUENTLY PLACED ON ITS ADJACENT MOUNTING BRACKET. |  |  | 4
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D20 PLUMBING | D2020 DOMESTIC WATER DISTRIBUTION | D202003 DOMESTIC WATER EQUIPMENT | Water Heaters, Commercial, Gas - 200 MBH input, 192 GPH | MECH WTR HTR COM GAS 1 | 2 | EA | 2007 | Input | 10 | 15 | -5 | 0 | FALSE |  | 39.6606 |  |  | MHMV008829 |  |  | D100L1993N | SC0830193 | 100 GAL 199 MBH 181.8 GPH RECOVERY | BRADFORD-WHITE |  | 2007 |  |  |  | BASE MECH RM |  |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D20 PLUMBING | D2020 DOMESTIC WATER DISTRIBUTION | D202003 DOMESTIC WATER EQUIPMENT | Water Heaters, Commercial, Gas - 200 MBH input, 192 GPH | MECH WTR HTR COM GAS 1 | 2 | EA | 2007 | Input | 10 | 15 | -5 | 0 | FALSE |  | 39.6606 |  |  | MHMV006815 |  |  | D100L1993N | WC8829070 | 100 GAL 199 MBH 181.8 GPH RECOVERY | BRADFORD-WHITE |  | 2007 |  |  |  | BASE MECH RM |  |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D20 PLUMBING | D2040 RAIN WATER DRAINAGE | D204003 RAINWATER DRAINAGE EQUIPMENT | Sump Pump - Submersible | MECH RNWTR DRN SUMP SUB 1 | 1 | EA | 2006 | Input | 25 | 16 | 9 | 4.1741 | FALSE |  | 56.6939 |  | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. | NA |  |  | NA | NA | NA | NA |  | 2006 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3010 ENERGY SUPPLY | D301002 GAS SUPPLY SYSTEM | Gas Meter | EXT GAS SUP MTR 1 | 1 | EA | 1987 | Input | 50 | 35 | 15 | 3.9784 | FALSE |  | 47.8691 |  |  | MHMV008838 |  |  | AL-800 | 85S6350219 | 800 CFH AT 0.5 IN DIFF | AMERICAN METER COMPANY |  | 1987 |  |  |  | SOUTH EXTERIOR |  |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3020 HEAT GENERATING SYSTEMS | D302001 BOILERS | Gas, Hot Water - 650-900 MBH | MECH BLR GAS HT WTR 1 | 1 | EA | 1987 | Input | 30 | 35 | -5 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. | MHMV008836 |  |  | NA | NA | 800 MBH EST | BURNHAM |  | 1987 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3020 HEAT GENERATING SYSTEMS | D302004 AUXILIARY EQUIPMENT | Expansion Tank - 24 gal | MECH AUX EXP TNK 1 | 1 | EA | 2006 | Input | 30 | 16 | 14 | 1.972 | FALSE |  | 46.4147 |  | [Matthew Vella on 11/13/2017 4:08:27 PM] THIS UNIT LACKED A DATA PLATE. | MHMV033955 |  |  | NA | NA | 20 GAL EST | NA |  | 2006 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 4:08:27 PM] THIS UNIT LACKED A DATA PLATE. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3030 COOLING GENERATING SYSTEMS | D303001 CHILLED WATER SYSTEMS | Chiller, Reciprocating, Air Cooled - 20 TN | EXT CHIL WTR RECIP AIR 1 | 1 | EA | 1987 | Input | 20 | 35 | -15 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2017 9:57:27 AM] THE DATA PLATE WAS REMOVED FROM THIS UNIT. | MHMV033980 |  |  | NA | NA | 33 TON EST | YORK |  | 1987 |  |  |  | SOUTH EXTERIOR | [Matthew Vella on 11/13/2017 9:57:27 AM] THE DATA PLATE WAS REMOVED FROM THIS UNIT. |  |  | 4
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3030 COOLING GENERATING SYSTEMS | D303004 AUXILIARY EQUIPMENT | Expansion Tank - 40 gal | MECH AUX EXP TNK 1 | 1 | EA | 1987 | Input | 19 | 35 | -16 | 0.86843 | FALSE |  | 44.5576 |  | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. | NA |  |  | NA | NA | 40 GAL EST | TACO |  | 1987 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3040 DISTRIBUTION SYSTEMS | D304001 AIR DISTRIBUTION, HEATING & COOLING | Air Separator - Air control, air separator, 2" diameter, includes strainer | MECH AIR SEP 1 | 1 | EA | 1987 | Input | 35 | 35 | 0 | 2.4736 | FALSE |  | 47.0058 |  | [Matthew Vella on 11/13/2017 1:14:00 PM] THE DATA PLATE WAS INACCESSIBLE. | MHMV033962 |  |  | NA | NA | 2 IN EST | TACO |  | 1987 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 1:14:00 PM] THE DATA PLATE WAS INACCESSIBLE. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3040 DISTRIBUTION SYSTEMS | D304003 HOT WATER DISTRIBUTION SYSTEMS | Circulating Pump, End Suction - 2-1/2" size, 3 HP, to 150 GPM | MECH HOT WTR CIRC PUMP 1 | 2 | EA | 2006 | Input | 20 | 16 | 4 | 0.96876 | FALSE |  | 44.7445 |  | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. | NA |  |  | NA | NA | 3 HP EST | NA |  | 2006 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3040 DISTRIBUTION SYSTEMS | D304003 HOT WATER DISTRIBUTION SYSTEMS | Circulating Pump, End Suction - 2-1/2" size, 3 HP, to 150 GPM | MECH HOT WTR CIRC PUMP 1 | 2 | EA | 2006 | Input | 20 | 16 | 4 | 0.96876 | FALSE |  | 44.7445 |  | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. | NA |  |  | NA | NA | 3 HP EST | NA |  | 2006 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3040 DISTRIBUTION SYSTEMS | D304006 CHILLED WATER DISTRIBUTION SYSTEMS | Circulating Pump, End Suction - 3" size, 5 HP, to 225 GPM | MECH CHIL WTR CIRC PUMP 1 | 2 | EA | 2006 | Input | 20 | 16 | 4 | 0.96876 | FALSE |  | 44.7445 |  | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. | NA |  |  | NA | NA | 3 HP EST | NA |  | 2006 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3040 DISTRIBUTION SYSTEMS | D304006 CHILLED WATER DISTRIBUTION SYSTEMS | Circulating Pump, End Suction - 3" size, 5 HP, to 225 GPM | MECH CHIL WTR CIRC PUMP 1 | 2 | EA | 2006 | Input | 20 | 16 | 4 | 0.96876 | FALSE |  | 44.7445 |  | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. | NA |  |  | NA | NA | 3 HP EST | NA |  | 2006 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 9:27:01 AM] BASED ON THE HAZARDOUS CONDITIONS IN THIS MECHANICAL ROOM, THE DATA PLATE WAS INACCESSIBLE. |  |  | 4
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES.
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES.
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305003 FAN COIL UNITS | Cab Mount, Four Pipe - 1 ton | INT FCU CAB4P 1 | 40 | EA | 1987 | Input | 15 | 35 | -20 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2014710:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. | NA |  |  | NA | NA | 1 TON | NA |  | 1987 |  |  |  | DORMS | [Matthew Vella on 11/13/2017 10:06:32 AM] DESPITE ALL EFFORTS, ACCESS TO EACH ROOM WAS NOT POSSIBLE. DATA FOR THE FAN COIL UNITS WAS COLLECTED FROM THE BCE DRAWINGS ARCHIVES. |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305004 FIN TUBE RADIATION | Baseboard Heating - 6' long | INT FTR BSBRD 1 | 3 | EA | 1987 | Input | 30 | 35 | -5 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2017 4:08:27 PM] THIS UNIT LACKED A DATA PLATE. | NA |  |  | NA | NA | 4 FT EST | NA |  | 1987 |  |  |  | FLR1, COMM RM | [Matthew Vella on 11/13/2017 4:08:27 PM] THIS UNIT LACKED A DATA PLATE. THE ROOM IN WHICH THIS UNIT WAS LOCATED WAS LOCKED BUT THE WINDOW WAS SHATTERED. DESPITE OUR EFFORTS, THE TEAM WAS UNABLE TO OBTAIN KEYS FOR THIS FACILITY. THIS UNIT COULD NOT BE BARCODED. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305004 FIN TUBE RADIATION | Baseboard Heating - 6' long | INT FTR BSBRD 1 | 3 | EA | 1987 | Input | 30 | 35 | -5 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2017 4:08:27 PM] THIS UNIT LACKED A DATA PLATE. | MHMV033951 |  |  | NA | NA | 4 FT EST | NA |  | 1987 |  |  |  | FLR2, JANITOR'S CLOSET | [Matthew Vella on 11/13/2017 4:08:27 PM] THIS UNIT LACKED A DATA PLATE. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D30 HVAC | D3050 TERMINAL & PACKAGE UNITS | D305004 FIN TUBE RADIATION | Baseboard Heating - 6' long | INT FTR BSBRD 1 | 3 | EA | 1987 | Input | 30 | 35 | -5 | 0 | FALSE |  | 10 |  | [Matthew Vella on 11/13/2017 4:08:27 PM] THIS UNIT LACKED A DATA PLATE. | NA |  |  | NA | NA | 4 FT EST | NA |  | 1987 |  |  |  | FLR2, LAUNDRY RM | [Matthew Vella on 11/13/2017 4:08:27 PM] THIS UNIT LACKED A DATA PLATE. THE ROOM IN WHICH THIS UNIT WAS LOCATED WAS LOCKED BUT THE WINDOW WAS SHATTERED. DESPITE OUR EFFORTS, THE TEAM WAS UNABLE TO OBTAIN KEYS FOR THIS FACILITY. THIS UNIT COULD NOT BE BARCODED. |  |  | 1
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4010 FIRE ALARM AND DETECTION SYSTEMS | D401001 FIRE ALARM DISTRIBUTION | Fire Alarm Control Panel, multizone (4) - non addressable | BASE FIRE FACP NADD 1 | 1 | EA | 2007 | Input | 20 | 15 | 5 | 5.1748 | FALSE |  | 66.0166 |  | [Matthew Vella on 11/13/2017 1:14:00 PM] THE DATA PLATE WAS INACCESSIBLE. | MHMV008827 |  |  | FS90 | NA | 12 ZONES | HONEYWELL |  | 2007 |  |  |  | BASE MECH RM | [Matthew Vella on 11/13/2017 1:14:00 PM] THE DATA PLATE WAS INACCESSIBLE. |  |  | 4
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4010 FIRE ALARM AND DETECTION SYSTEMS | D401002 FIRE ALARM DEVICES | Annunciator | EXT FIRE ANNUN 1 | 7 | EA | 2007 | Input | 20 | 15 | 5 | 5.1748 | FALSE |  | 66.0166
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4010 FIRE ALARM AND DETECTION SYSTEMS | D401002 FIRE ALARM DEVICES | Bell signaling device | EXT FIRE BELL 1 | 1 | EA | 2007 | Input | 20 | 15 | 5 | 5.1748 | FALSE |  | 66.0166
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4010 FIRE ALARM AND DETECTION SYSTEMS | D401002 FIRE ALARM DEVICES | Manual pull station | EXT FIRE PULL 1 | 6 | EA | 1985 | Input | 20 | 37 | -17 | 5.1748 | FALSE |  | 66.4417
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4010 FIRE ALARM AND DETECTION SYSTEMS | D401002 FIRE ALARM DEVICES | Strobe/Annunciator Combo | EXT FIRE ST COMB 1 | 1 | EA | 2007 | Input | 20 | 15 | 5 | 5.1748 | FALSE |  | 66.0166
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4010 FIRE ALARM AND DETECTION SYSTEMS | D401002 FIRE ALARM DEVICES | Detectors with brackets, fixed temperature heat detector | SYS FIRE HT DET 1 | 107 | EA | 2007 | Input | 20 | 15 | 5 | 7.2385 | FALSE |  | 75.7558
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4010 FIRE ALARM AND DETECTION SYSTEMS | D401002 FIRE ALARM DEVICES | Detectors with brackets, ion detector (smoke) detector | SYS FIRE ION DET 1 | 40 | EA | 1985 | Input | 20 | 37 | -17 | 7.2385 | FALSE |  | 76.2348
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4020 FIRE SUPP WATER SUPPLY / EQUIP | D402001 FIRE PROTECTION WATER PIPING AND EQUIPMENT | Backflow Preventer - 6" | MECH FIRE BACKFLO PREV 1 | 1 | EA | 2007 | Input | 40 | 15 | 25 | 0 | FALSE |  | 30 |  |  | MHMV033978 |  |  | 880V | N0702050802 | 6 IN | FEBCO |  | 2007 |  |  |  | NORTH EXTERIOR |  |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4030 STANDPIPE SYSTEMS | D403001 STANDPIPE EQUIPMENT & PIPING | Riser - 4" diam | FLR1 FIRE RISER 1 | 1 | EA | 2007 | Input | 20 | 15 | 5 | 5.1748 | FALSE |  | 66.0166 |  | [Matthew Vella on 11/13/2017 1:14:00 PM] THE DATA PLATE LACKED REQUIRED INFORMATION. | MHMV033948 |  |  | NA | NA | 4 IN | ALLIANCE |  | 2007 |  |  |  | RM 238 | [Matthew Vella on 11/13/2017 1:14:00 PM] THE DATA PLATE LACKED REQUIRED INFORMATION. |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D40 FIRE PROTECTION | D4040 SPRINKLERS | D404001 SPRINKLERS AND RELEASING DEVICES | Wet Pipe Systems - light hazard | FLR1 FIRE WET LIT 1 | 15840 | SF | 2007 | Input | 75 | 15 | 60 | 22.2891 | FALSE |  | 69.2104
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501001 MAIN TRANSFORMERS | General | EXT XFRM MAIN 1 | 225 | KVA | 1990 | Input | 50 | 32 | 18 | 19.6692 | FALSE |  | 78.3056 |  |  | MHMV033516 |  |  | NA | P496052TOD | 225 KVA | GENERAL ELECTRIC |  | 1990 |  |  |  | SOUTH EXTERIOR |  |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501002 SERVICE ENTRANCE EQUIPMENT | Electrical Service - 3 Phase, 120/208 V, 800 A | EXT SERV 3 PHASE | 1 | EA | 1990 | Input | 35 | 32 | 3 | 2.4626 | FALSE |  | 46.9648 |  |  | MHMV033519 |  |  | TC723674 | NA | 800 A | GENERAL ELECTRIC |  | 1990 |  |  |  | SOUTH EXTERIOR |  |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501002 SERVICE ENTRANCE EQUIPMENT | Other | EXT SERV MTR 1 | 1 | AMP | 1990 | Input | 35 | 32 | 3 | 13.4539 | FALSE |  | 77.7123 |  |  | MHMV033515 |  |  | A3TL | 08394817 | 2.5 A | ELSTER GROUP |  | 1990 |  |  |  | SOUTH EXTERIOR |  |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Switchgear - 800 Amp | BASE PNLBRD SWTCHGR 1 | 1 | EA | 2005 | Input | 50 | 17 | 33 | 0 | FALSE |  | 10 |  |  | MHMV033514 |  |  | NA | NA | 800 A | GENERAL ELECTRIC |  | 2005 |  |  |  | BASEMENT |  |  |  | 4
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Switchgear - 800 Amp | BASE PNLBRD SWTCHGR 2 | 1 | EA | 2005 | Input | 50 | 17 | 33 | 0 | FALSE |  | 10 |  |  | MHMV033531 |  |  | NA | NA | 800 A | GENERAL ELECTRIC |  | 2005 |  |  |  | BASEMENT |  |  |  | 5
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | EXT PNLBRD SFTY SWTCH 1 | 2 | EA | 2005 | Input | 40 | 17 | 23 | 11.3982 | FALSE |  | 68.2779
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 400 Amp | EXT PNLBRD SFTY SWTCH 2 | 1 | EA | 1990 | Input | 40 | 32 | 8 | 11.3982 | FALSE |  | 68.5699 |  |  | MHMV035909 |  |  | NA | NA | 400 A | SQUARE D |  | 1990 |  |  |  | SOUTH EXTERIOR |  |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 1 | 1 | EA | 2005 | Input | 40 | 17 | 23 | 0 | FALSE |  | 30 |  |  | MHMV033950 |  |  | NA | NA | 225 A | GENERAL ELECTRIC |  | 2005 |  |  |  | 1ST FLR ELEC RM |  |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 2 | 1 | EA | 2005 | Input | 40 | 17 | 23 | 0 | FALSE |  | 30 |  | [Adam Nodel on 11/30/2017 4:20:32 PM] NO DATA PLATE WAS AVAILABLE FOR THIS PANELBOARD. ALL RATINGS ARE ESTIMATED. | MHMV033949 |  |  | NA | NA | 225 A | GENERAL ELECTRIC |  | 2005 |  |  |  | 1ST FLR ELEC RM
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 3 | 1 | EA | 2005 | Input | 40 | 17 | 23 | 0 | FALSE |  | 30 |  | [Adam Nodel on 11/30/2017 4:20:32 PM] NO DATA PLATE WAS AVAILABLE FOR THIS PANELBOARD. ALL RATINGS ARE ESTIMATED. | MHMV033593 |  |  | NA | NA | 225 A | GENERAL ELECTRIC |  | 2005 |  |  |  | 1ST FLR ELEC RM
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR1 PNLBRD MAIN 4 | 1 | EA | 2005 | Input | 40 | 17 | 23 | 0 | FALSE |  | 30 |  | [Adam Nodel on 11/30/2017 4:20:32 PM] NO DATA PLATE WAS AVAILABLE FOR THIS PANELBOARD. ALL RATINGS ARE ESTIMATED. | MHMV033592 |  |  | NA | NA | 225 A | GENERAL ELECTRIC |  | 2005 |  |  |  | 1ST FLR ELEC RM |  |  |  | 2
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR2 PNLBRD MAIN 1 | 1 | EA | 2005 | Input | 40 | 17 | 23 | 0 | FALSE |  | 30 |  |  | MHMV040341 |  |  | NA | NA | 225 A | GENERAL ELECTRIC |  | 2005 |  |  |  | 2ND FLR ELEC RM |  |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR2 PNLBRD MAIN 2 | 1 | EA | 2005 | Input | 40 | 17 | 23 | 0 | FALSE |  | 30 |  |  | MHMV040342 |  |  | AQF3302MBX | NA | 225 A | GENERAL ELECTRIC |  | 2005 |  |  |  | 2ND FLR ELEC RM |  |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 225 amp, NQOD | FLR2 PNLBRD MAIN 3 | 1 | EA | 2005 | Input | 40 | 17 | 23 | 0 | FALSE |  | 30 |  |  | MHMV040343 |  |  | NA | NA | 225 A | GENERAL ELECTRIC |  | 2005 |  |  |  | 2ND FLR ELEC RM |  |  |  | 3
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Exit Lighting | EXT LTNG EXIT 1 | 4 | EA | 2005 | Input | 25 | 17 | 8 | 0 | FALSE |  | 30
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Exterior Lighting | EXT LTNG EXT 1 | 46 | EA | 2005 | Input | 25 | 17 | 8 | 9.3103 | FALSE |  | 76.5775
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Interior Lighting, Fluorescent | INT LTNG FLUOR 1 | 140 | EA | 2005 | Input | 20 | 17 | 3 | 7.2385 | FALSE |  | 75.8482
ABANDONED FACILITIES | 01911 | VOQ (O1-O10) | 1965 | 17538 | SF | 2 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Interior Lighting, Incandescent | INT LTNG INCAN 1 | 52 | EA | 2005 | Input | 20 | 17 | 3 | 5.1748 | FALSE |  | 66.0988
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2010 EXTERIOR WALLS | B201001 EXTERIOR CLOSURE | Stucco | EXT WALL STUC 1 | 1287 | SF | 1990 | Estimated | 40 | 32 | 8 | 12.2265 | FALSE |  | 70.7564
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2030 EXTERIOR DOORS | B203001 SOLID DOORS | Aluminum | EXT DR AL 1 | 1 | EA | 1990 | Estimated | 20 | 32 | -12 | 0 | FALSE |  | 39.0982
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | B20 EXTERIOR ENCLOSURE | B2030 EXTERIOR DOORS | B203001 SOLID DOORS | Aluminum | EXT DR AL 1 | 2 | EA | 1990 | Estimated | 20 | 32 | -12 | 3.9394 | FALSE |  | 61.2701
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | B30 ROOFING | B3010 ROOF COVERINGS | B301002 LOW SLOPE ROOF SYSTEMS | Built-Up | ROOF LOW BLT UP 1 | 500 | SF | 2010 | Estimated | 20 | 12 | 8 | 3.9394 | FALSE |  | 58.9582
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | C10 INTERIOR CONSTRUCTION | C1010 PARTITIONS | C101001 FIXED PARTITIONS | Wall - Concrete Block | INT PART CON BLK 1 | 128 | SF | 1970 | Input | 75 | 52 | 23 | 26.729 | FALSE |  | 75.188
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501002 SERVICE ENTRANCE EQUIPMENT | Other | EXT SERV MTR 1 | 1 | AMP | 2010 | Input | 35 | 12 | 23 | 14.0542 | FALSE |  | 77.0011 |  |  | MHMV003507 |  |  | ZD3300K0082 03 | 08298282 | 30 A | ELSTER |  | 2010 |  |  |  | NORTH EXTERIOR |  |  |  | 2
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Main lugs, 120/208 V, 100 amp, NQOD | INT PNLBRD MAIN 1 | 1 | EA | 1985 | Input | 40 | 37 | 3 | 0 | FALSE |  | 10 |  | [Adam Nodel on 1/22/2018 9:27:08 AM] THE DATA PLATE ON THIS PANELBOARD WAS ILLEGIBLE. | MHMV039308 |  |  | NA | 1303 | 100 A | CUTLER HAMMER |  | 1985 |  |  |  | MAIN ROOM |  |  |  | 2
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 200 Amp | INT PNLBRD SFTY SWTCH 1 | 1 | EA | 1985 | Input | 40 | 37 | 3 | 12.2265 | FALSE |  | 70.9738 |  |  | MHMV003509 |  |  | NA | NA | 200 A | SQUARE D |  | 1985 |  |  |  | NORTH EXTERIOR |  |  |  | 2
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | D50 ELECTRICAL | D5010 ELECTRICAL SERVICE & DISTRIBUTION | D501004 PANELBOARDS | Safety Switch, 30-100 Amp | INT PNLBRD SFTY SWTCH 2 | 1 | EA | 1985 | Input | 40 | 37 | 3 | 3.9911 | FALSE |  | 49.9678
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502001 BRANCH WIRING | General | INT ELEC BRANCH WRNG 1 | 407 | SF | 1970 | Input | 60 | 52 | 8 | 20.5137 | FALSE |  | 74.1384
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Exterior Lighting | EXT LTNG EXT 1 | 1 | EA | 1985 | Input | 25 | 37 | -12 | 6.0112 | FALSE |  | 65.4873
TO BE DEMOED | 01912 | SWIM POOL WTR TRMT | 1970 | 407 | SF | 1 | D50 ELECTRICAL | D5020 LIGHTING & BRANCH WIRING | D502002 LIGHTING EQUIPMENT | Explosion Proof Lighting | INT LTNG EXPL 1 | 8 | EA | 1985 | Input | 20 | 37 | -17 | 3.9394 | FALSE |  | 61.4527